INSTALLATION GUIDE

[ 0095311 ]

This document may not be copied, reproduced or distributed in any form or by any means whatsoever without our prior consent. Whilst care has been taken to ensure accuracy we do not assume responsibility for the consequences of any errors or omissions that may be contained herein. This document does not constitute any form of agreement or contract.

STATEMENT OF "CE" COMPLIANCE

The undersigned manufacturer:

ELOTEC EURL    Boulevard du Midi    47160 DAMAZAN

hereby declares that the computer product  manufactured and supplied under the registered trademark of:

MCU PLUS

complies with:

the regulations defined by European Directive 89/336/CEE

Statement made at:	DAMAZAN

On:			Monday, 31/January/2000

By: 			Mr. ERIC LONCKE

Sole proprietor and manager

COVER PAGES			Pages 1 & 2

DECLARATION OF  ‘CE’	CONFORMITY	3

CONTENTS			4 & 5

OVERVIEW

- Purpose of this guide		6

- Safety			6

- MCU Plus and Extension	7

Schematic diagram	8

INPUT / OUTPUT CONNECTIONS

- Terminal boards		9

(i) Universal connection board	9

(ii) Connection board for 32IN	10

(iii) Connection board with Auto /Manual switching	11

(iv) Unused wires	12

- Low-voltage distribution		12

8IN /8OUT /1COUNTER(PULSE)

- Layout and connections		13

16IN (ANALOG)

- Layout and connections		14

32IN (ANALOG) + 2COUNTER (PULSE)

- Layout and connections		15

- Input current limits		17

- Analog output (available only as an option)	17

8 COUNTER (PULSE) INPUTS

- Layout and connections		18

16 OUTPUTS (ON/OFF)

- Layout and connections		19

32 OUTPUTS (ON/OFF)

- Layout and connections		19

LIQUID NUTRIENT CONTROL (3IN + 3OUT)

- Layout and connections		20

GENERAL SENSOR CONNECTIONS

- Diagram			21

CONFIGURABLE SENSOR INPUTS

- Summary table		22

FIFO BOARD (RS-485 SERIAL LINK)

- Description			23

- Connection			23

RS232 BOARD (SERIAL LINK)

- Description			24

- Connections			24

INTERNAL MBIN BUS

- Description			25

- Short bus			25

- Long bus			26

- Declaring I / O boards		27

POWER SUPPLIES

- Power distribution schematic	28

- External components		29

- Internal components		29

(i) DC fuses	29

(ii) Extension power supplier	30

- Power supplier sub-chassis	30

(i) Triple power supplier (MCU Plus)	31

(ii) Low-voltage supply	31

- Checking the ‘Watchdog’ alarm	32

LFP-03 BOARD CONFIGURATION

- Layout			33

- Memory			33

GENERAL SPECIFICATIONS

- I/O board characteristics		34

- Electrical			35

- Mechanical			35

- Wall mounting			35

(blank page)	36

REVISIONS 		(not normally included)	37

- Purpose of this guide

This document is intended for system installers and, therefore, only properly qualified personnel should refer to it in the course of carrying out technical work.

This guide does not contain step-by-step installation and set-up instructions. It includes reference information in the form of schematics, wiring diagrams and other illustrations in enough detail to enable experienced personnel to install, connect up, and check the hardware configuration of the controller.

This guide should be used in conjunction with the following related documents:

‘Program input / output list’

‘Sensors – Installation’

‘User’s programming guide’.

Detailed fault-finding and repair instructions are also not included in this guide. Any components judged to be malfunctioning must be returned to Femco for investigation through our usual procedures.

- Safety

Always work safely and observe all relevant safety regulations when installing, operating, or servicing the equipment.

Fuses

Always ensure the controller is turned OFF before removing or inserting fuses.

- MCU Plus and Extension

Schematic diagram

- Terminal boards

The wiring for sensor inputs and control outputs is connected to the MCU Plus via terminal boards, normally used in pairs, that plug into the sockets fitted to each host I/O board.

(i) Universal connection board

This board is used with all types of input or output board with the exception of the 32IN board. The legends on either side of the terminal blocks identify eight groups of three terminals, which may be used for input, output or external power supply connections depending on the type of host board.

(ii) Connection board for 32IN

Separate blocks are provided on this board for the input, ground (0V), and sensor supply voltage terminals. The terminals for the pulse input and analog output (rarely implemented) are on the same block.

(iii) Connection board with Auto /Manual switching

This board can be used with the 16 On/Off output board only and offers the possibility of Auto or Manual operation of the outputs. Auto corresponds to normal output switching by the host board relay, manual operation allows an output to be forced ON or OFF (Stop) independently of the relay. Note that only the normally open (NO) relay contacts are switched and, except for output 1, the normally closed (NC) are not available. (The output 1 NC contact is brought out directly to a separate terminal).

A three-position switch selects the operating mode of each output. A pair of LEDs indicate the state of each switch: in auto mode the green LED is illuminated, in manual ON mode the red LED is illuminated, and with the switch in the Stop position the LEDs and the output are all OFF.

(iv) Unused wires

After all inputs and outputs have been connected, any spare control wiring should ideally be identified, labeled and isolated at both ends. If space permits, the MCUPlus offers the possibility of connecting unused wires to ground using the terminal block provided inside the machine.

- Low-voltage distribution

- Layout and connections

Note: the pulse input requires a bridge (strap) between the two connection boards.

The characteristics of this board are included in the table on page 37. Refer also to the guide entitled Sensors – Installation, which contains full connection and calibration details for individual sensors.

- Layout and connections

The characteristics of this board are included in the table on page 37. Refer also to the guide entitled Sensors – Installation, which contains full connection and calibration details for individual sensors.

- Layout and connections

The characteristics of this board are included in the table on page 37. Refer also to the guide entitled Sensors – Installation, which contains full connection and calibration details for individual sensors.

- Input current limits

Total current consumption from the Vref supply must not exceed 25mA per group of sixteen inputs.

| Sensor | Current | Current |
| --- | --- | --- |
|  | [supply = +15V] | [supply = Vref] |
| Ec | 0.12A | 0A |
| pH | 0.08A | 0A |
| Solarimeter | 0.025A | 0A |
| RH | 0.025A | 0A |
| Temperature | 0A | 0.25mA |
| Wind vane | 0A | 0.25mA |
| Vent position | 0.5mA | 0A |
| Rain sensor | 0A | 0A |
| Flow sensors | 0.025A | 0A |

- Analog output (available only as an option)

- Layout and connections

The characteristics of this board are included in the table on page 37. Refer also to the guide entitled Sensors – Installation, which contains full connection and calibration details for individual sensors.

- Layout and connections

The characteristics of this board are included in the table on page 37.

- Layout and connections

The characteristics of this board are included in the table on page 37.

- Layout and connections

The characteristics of this board are included in the table on page 37.

- Diagram

Refer also to the guide entitled Sensors – Installation, which contains full connection and calibration details for individual sensors.

- Summary table

|  | TYPE OF I/P BOARD  |  |  | 8IN /8OUT /1C & 16IN |  |  |  |  | 32IN |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | TYPE OF SENSOR  | S1 |  |  | S2 | S3 | S4 |  | JUMPER |  | SUPPLY VOLTAGE |
|  | O/s T° (NTC) | ON |  |  | OFF | OFF | OFF |  | Blue |  | REF |
|  | Amb. T° (NTC) | ON |  |  | OFF | OFF | OFF |  |  |  | REF |
|  | RH (NTC) | ON |  |  | OFF | OFF | OFF |  |  |  | REF |
|  | Contact | ON |  |  | OFF | OFF | OFF |  |  |  | REF |
|  | Reserved | ON |  |  | OFF | OFF | OFF |  |  |  | x |
|  | Current loop 4..20mA | OFF |  |  | ON | OFF | OFF |  | Red |  | +15V |
|  | Current loop 0..20mA | OFF |  |  | ON | OFF | OFF |  |  |  | +15V |
|  | Current loop 5..25mA | OFF |  |  | ON | OFF | OFF |  |  |  | +15V |
| With | Ec | OFF |  |  | ON | OFF | OFF |  |  |  | +15V |
| amplifier | pH | OFF |  |  | ON | OFF | OFF |  |  |  | +15V |
|  | HR (electronic) | OFF |  |  | ON | OFF | OFF |  |  |  | +15V |
|  | CO2 | OFF |  |  | ON | OFF | OFF |  |  |  | N/a |
|  | Rain detection | OFF |  |  | ON | OFF | OFF |  |  |  | N/a |
|  | Solarimeter | OFF |  |  | ON | OFF | OFF |  |  |  | +15V |
|  | Current loop 0..4mA | OFF |  |  | OFF | ON | OFF |  | Yellow |  | N/a |
|  | Wind vane (0..1000) | OFF |  |  | OFF | ON | OFF |  |  |  | REF |
|  | TEPVA | OFF |  |  | OFF | ON | OFF |  |  |  | REF |
|  | Water T° (NTC) | OFF |  |  | OFF | OFF | ON |  | Green |  | REF |
|  | TAPVA | OFF |  |  | OFF | OFF | ON |  |  |  | REF |
|  | Wind vane (0..20k = default) | OFF |  |  | OFF | OFF | OFF |  | x |  | REF |
|  | 0 - 5V | OFF |  |  | OFF | OFF | OFF |  | Green |  | N/a |
|  | Vent position | OFF |  |  | OFF | OFF | OFF |  | x |  | REF |
|  | Vent position (32-IN board) | x |  |  | x | x | x |  | Blue |  | +15V |

Refer also to the guide entitled Sensors – Installation, which contains full connection and calibration details for individual sensors.

- Description

The board allows an MCU Plus controller to communicate with a suitably equipped host PC sited up to 1,200 meters away. The RS-485 standard allows several controllers to be connected to the link (multi-drop).

NOTE: line terminating jumpers must be in place on the 2 boards at the network extremities. (Check the PC comms board also in this regard).

- Connection

- Description

This board provides a serial interface for the MCUPlus controller enabling it to exchange data with a suitably equipped PC.

The common (Gnd) and data (Tx, Rx) categories of the RS-232 standard are implemented. The RTS signal can also be used to provide a minimum of control (handshaking), if required.

NOTE: although the board is physically capable of providing two data links, link 2 is reserved for future development and cannot be used.

- Connections

- Description

The MBIN bus is the interface between the main microprocessor board and peripheral input /output boards. It carries data signals and power supply voltages. The ‘short bus’ board, fitted only within the main MCUPlus controller, can be extended by means of ‘long bus’ boards fitted within one or more extension units.

IRQs

Each occupied slot on the MBIN bus is given an IRQ address, of which there are 16 possible values. This allows the bus to recognize the presence of the in /out board occupying the slot. Several slots can share the same IRQ provided they are consecutive from left to right on the bus. For example, on the long bus:

| Slot | A | B | C | D | E | F |
| --- | --- | --- | --- | --- | --- | --- |
| IRQ address | 5 | 6 | 7 | 7 | 7 | 8 |

NOTE: the correspondence between slot IRQ addresses and the I/O boards occupying the slots may be viewed and, if necessary, reconfigured in the installation menu shown on page 29.

- Short bus

NOTE

Slots A and B on this board always have addresses IRQ 1 and IRQ 2, respectively.

- Long bus

Jumper configuration

Three sets of jumpers are involved in the configuration of each slot address on a long bus:

– the IRQ number required by the system to detect and use the slot,

– the slot address sharing jumpers defining the range of the IRQ in terms of the previous and next slots (see table opposite for coherence),

– the ‘service’ jumpers defining the IRQs used on the current board and any boards downstream.

Example:

In the illustration IRQ3 starts at slot A and extends to slot D; IRQ4 starts at slot E and extends to slot F and the next long bus board, on which IRQ5 is also in service.

- Declaring I/O boards

The menu shown below enables you to check that the MBIN bus software configuration matches the type and number of installed input /output boards.

Note: changes are only necessary if the system’s in/out board profile is changed on site (to add or remove boards, for example). Any configuration changes are permanently stored in memory.

Board types

8E/8S/1C		= 8 Inputs, 8 Outputs, 1 Counter (pulse)

8 Compteurs 		= 8 Counter Inputs

16 Entrées		= 16 Analog Inputs

32 Entrées		= 32 Analog Inputs

16 Sorties		= 16 On /Off  Outputs

3 Eng. Li		= 3 Liquid Nutrients (flow sensor + solenoid valve control)

NOTES :

i) Depending on board type the maximum number per IRQ is:

for types   8-E/8-S/1-C, 16 Entrées, et 3 Eng. Liq.	1 board

for type     8 Compteurs			 	4 boards

for  type    16 Sorties				16 boards.

ii)  IRQ 1 and 2 are reserved for the short bus.

iii) The 32S (32 O/ps) board must be declared as: Type = 16 Sorties, No. boards = 2.  1

- Power distribution schematic

NOTE: if a second power supplier, 0/+15V, is fitted inside the controller (rare) it alone supplies the +15V to the machine (the TF-442 continues to supply +5V and -15V). Extension units have their own 0/+15V power suppliers, as shown above.

- External components

Always ensure the controller is turned OFF before removing or inserting a fuse!

- Internal components

(i) DC fuses

The fuses for the main DC supply rails are accessible when the MCU Plus top cover is in the raised position.

(ii) Extension power supplier

To access this board, unlock and maintain the Extension Unit top cover in the raised position, and remove the slotted cover plate (two fixing screws).

Note: a second board may be fitted if required.

- Power supplier sub-chassis

The remaining components of the power supplier unit, which do not include easily replaceable parts, are fitted beneath a sub-chassis within the main case. In the unlikely event that access to these parts is required, the sub-chassis may be completely removed as shown in the illustration below (although the fixings may vary slightly between the different models of case).

(i) Triple power supplier (MCU Plus)

(ii) Low-voltage supply

- Checking the ‘Watchdog’ alarm

The watchdog function suspends control of the installation if the controller becomes incapable of managing of the system due to either an electronic or software malfunction. The alarm also monitors the status of the 24V low-voltage output. If an alarm condition occurs an audible warning is sounded and the 24V low-voltage supply output is disconnected. Once triggered, the alarm must be rearmed manually in order to reset it to the guard status.

Procedure

Turn the machine OFF and remove one of the L-V fuses. On switching the machine back ON the green LED will not illuminate, indicating that there is no 24V L-V supply. After approximately 10 seconds an audible warning is heard. At the same time, the alarm output switches over from the NC (=normally closed) to NO (=normally open) contacts, as shown in the diagram.

To reset the alarm, first switch OFF the machine before replacing the fuse. Turn the machine ON and press the reset button inside the controller. The alarm is now rearmed.

IMPORTANT

The alarm output is rated at 50mA/24VAC max and is intended for low power applications only. It must not be used to drive power control relays or similar devices.

- Layout

- Memory

program

data

|  |  | J2 | J3 | J4 | J6 | Memory |
| --- | --- | --- | --- | --- | --- | --- |
|  |  |  |  |  |  | - program 4 Megabits |
| FERTI |  |  |  |  |  | - data 2 Megabits |
|  |  |  |  |  |  | - program 8 Megabits |
| CLIMAT |  |  |  |  |  | - data 2 Megabits |
|  |  |  |  |  |  | - program 8 Megabits |
| GLOBAL |  |  |  |  |  | - data 4 Megabits |

|  | J5 | J8 | J9 | J12 | J13 | J14 | J15 | J16 | J21 | J29 | J30 | J31 | J33 | J34 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Unchanged |  |  |  |  |  |  |  |  |  |  |  |  |  |  |

- I/O board characteristics

| Type | Characteristics | Specifications | Comments |
| --- | --- | --- | --- |
| 8E/8S/1C | 8 analog inputs | 10-bit resolution (LFP board) |  |
| (8I/8O/1C) |  | Configurable for sensors | DIP switches |
|  |  | Sensor supply voltages: +15V and Vref | DIP switches |
|  |  |  | Vref = 5V |
|  | 8 On /Off outputs | Relays: 8RT, 2A /24VAC or DC |  |
|  |  | O/p 7 & 8 selectable (NO or NC) | jumper configured |
|  | 1 pulse input | Dry contact |  |
|  | 8 LED indications | Status of outputs |  |
|  |  | Power supply: +15V | NOTE: via LFP board |
| 16E | 16 analog inputs | 10-bit resolution |  |
| (16I) |  | Configurable for sensors | DIP switches |
|  |  | Sensor supply voltages: +15V and Vref | DIP switches |
|  |  |  | Vref = 5V |
|  |  | Power supply: +15V | via MBIN bus |
| 32E | 32 analog inputs | 10-bit resolution |  |
| (32I) |  | Configurable for sensors | colored jumpers |
|  |  | Sensor supply voltages: +15V and Vref | Imax = 25mA per 16 i/ps |
|  |  |  | Vref = 2.5V |
|  | 2 pulse inputs | Dry contact or open collector | 256 pul. /sec max |
|  | 2 analog outputs | 0..20mA current loop | NOTE: * OPTIONAL * |
|  |  |  | opto-isolated |
|  |  | Power supply: +15V | via MBIN bus |
| 8EC | 8 pulse inputs | Dry contact or open collector | max frequency = 256Hz |
| (8CI) |  | Power supply: 24VDC or 24VAC | via terminals |
| 16S | 16 On /Off outputs | Relays: 16RT, 2A /24VAC or DC |  |
| (16O) | 16 LED indications | Outputs |  |
|  |  | Power supply: +15V | via MBIN bus |
| 32S | 32 On /Off outputs | 32T, 6A /24VAC or DC | 2 groups of 16 outputs |
| (32O) |  | Power supply: +15V | via MBIN bus |
| Eng. Liquides | 6 pulse inputs | 3 flow sensor (+ 3 check) inputs | max frequency = 1500Hz |
| (Liquid Nutrient |  |  | NOTE: check i/ps reserved |
| line control) | 3 On/Off outputs | Relays: 3T, 2A /24VAC or DC |  |
|  |  | Low-voltage supply: on-board or external | jumper configured |
|  |  | Power supply: 24VDC or 24VAC | via terminals |
| COMMS |  |  |  |
| RS232 | 2 lines | Conforms to RS232 standard | NOTE : line 2 is reserved |
|  |  | Half-duplex transmission |  |
|  |  | Max. distance = 15 m |  |
|  |  | 9600 baud |  |
|  |  | Over-voltage protection |  |
| FIFO (RS485) | 1 line | Conforms to RS485 standard |  |
|  |  | Half-duplex transmission | uses on-board protocol |
|  |  | Overall max. distance = 1,200 m |  |
|  |  | 19200 baud |  |
|  |  | Opto-isolated |  |

- Electrical

Power supply			: 230VAC / 50Hz  (for other options consult Femco)

Current consumption		: 0.75A max

Power supplier line fuse		: 3.15A/250VAC

On-board power supplier fuse	: T4A L /250VAC

L-V supply fuses    25VA		: Pri:  - T150mA L		Sec - T1.5A L

63VA		:         - T315mA L	       	       - T3.15A L

100VA		:         - T500mA L		       - T5A L.

- Mechanical

Dimensions		: 	42cm (W), 40cm (H), 17cm (D)

Weight		: 	…kg

IP		: IP64

- Wall mounting

This page is left blank intentionally

| N° | Details | Date |
| --- | --- | --- |
| 1 | Ver.A: new MCUPlus installation guide. No copies were circulated before an | 30/09/2003 |
|  | updated version for (possible!) distribution with each machine was produced. | 24/12/2003 |
|  | (as per Start, Planet,and MBEX). |  |
| 2 | Ver. A1: the table on page 31 was updated with supply voltage = n/a for sensors | 28/01/2004 |
|  | Rain, 0-5V and 0..4mA current loop output . (no copies of A or A1 issued to date, |  |
|  | copies awaiting release corrected by hand). |  |
| 3 | Corrections and minor explanations added. Version A2 created. | 05/01/2004 |
| 4 | Agriware version created. No other modifications made. Version A3. | 01/06/2004 |
| 5 | Drawing details changed: Overview pt3 and FIFO board pt 2. Version A4. | 20/09/2004 |
| 6 | Watchdog alarm explained, check procedure modified slightly | 30/08/2005 |